## Slide 1: Essentials of Surface Water Treatment (Part 1 of 2)
Oregon Health Authority
Drinking Water Services
www.healthoregon.org/dwp

## Slide 2: Overview of Course:
Part 1
Background of Surface Water Treatment Rules
Filtration
Disinfection
Operations
Part 2
Review of Part 1
Reporting Requirements
Emerging Issues
Resources for Operators

## Slide 3: Regulations protect the public from exposure to pathogens:
Protozoa or Parasites
  Giardia Lamblia Cryptosporidium Parvum
Bacteria
  Campylobacter, Shigella, Legionella
Viruses
  Hepatitis A, Norwalk Agents

## Slide 4: Oregon Waterborne Disease Outbreaks (bacteria, viruses, parasites )
Chart: Total Cases, 26 Outbreaks-7,000 sickened (CDC)
| 1970s (federal Act) | 1980s (State Act, Primacy) | 1990s (federal revolving fund) | 2000s (new EPA standards)
 | 15 | 6 | 3 | 2
~50% drop
~50% drop
Notes: 7,000 people sickened by Oregon’s Public Drinking Water

## Slide 5: Waterborne Disease Outbreak Causes
Chart: 
| Contaminated water source, no treatment | Treatment inadequacies | Miscellaneous unknown causes | Distribution system deficiencies
Waterborne disease outbreak causes | 0.13 | 0.48 | 0.07 | 0.32
From August 2006 Access AWWA
Most of these outbreaks involve microbiological agents that would respond to proper disinfection

## Slide 6: Filtration is key to preventing waterborne disease outbreaks
Common types of water filtration systems:
  Conventional Filtration (CF) & Direct Filtration (DF) – a.k.a. “Rapid Rate”
  Slow sand
  Membrane
  Cartridge/bag
  Diatomaceous Earth (DE)
We’ll learn more about these later.

## Slide 7: Background of Surface Water Treatment Rules
1989 SWTR
Surface Water Treatment Rule
Required filtration for most SW and GWUDI (Groundwater Under Direct Influence).
  States were required to identify GWUDI sources.
Required pathogen removal/inactivation:
  3-log Giardia (99.9%) & 4-log virus (99.99%)
Limited turbidity in filtered water (combined filter effluent):
  Slow sand/DE/membrane/cartridge/bag:
    95% of turbidity readings ≤ 1 NTU; all < 5 NTU
  CF/DF:
    95% of turbidity readings ≤ 0.5 NTU; all < 5 NTU (replaced under LT1)
Required detectable disinfectant residual.
Did not address Cryptosporidium.

## Slide 8: U.S. Outbreaks of Cryptosporidiosis in Surface Water Supplies
Five of the outbreaks were associated with filtered drinking waters.
Three systems (Carroll, Jackson - Talent, and Milwaukee) were experiencing operational deficiencies and high finished water turbidities at the time of the out­breaks. All three plants utilized conventional treatment processes that included rapid mix, flocculation, sedimentation, and filtration.
The Clark County outbreak was the only outbreak associated with a filtered drinking water for which no treatment deficiencies were noted.
All five systems were in compliance with the federal regulations in effect at that time.

## Slide 9
(US)
Milwaukie, WI (Crypto)

## Slide 10: Background (continued)
1998 IESWTR
    Interim Enhanced Surface Water Treatment Rule
  Addressed concerns about Cryptosporidium
    required 2-log Crypto (99%) removal)
  Lowered turbidity standard for CF/DF systems:
    95% of readings ≤ 0.3 NTU, all readings <1 NTU for systems with population ≥10,000 (later extended to all CF/DF systems under LT1)
  Required Individual Filter Effluent (IFE) turbidimeters

## Slide 11: Background (continued)
2002 LT1
Long-Term 1 Enhanced SW Treatment Rule
  Extended 0.3 NTU requirement to CF/DF systems with <10,000 population.
2006 LT2 Long-Term 2 Enhanced SW Treatment Rule
  Requires additional Crypto treatment for systems with ≥ 0.075 oocysts/L in their source water.
  Very few systems are required to install additional treatment in Oregon.

## Slide 12: Why Measure Turbidity?
Indicative of pathogen removal
Relatively easy to monitor
Turbidity removal has been shown to be directly related to removal of Giardia and Crypto.
Turbidity maximum contaminant levels (MCLs) are based on the technology used:
  ≤ 0.3 NTU (95% of the time) for conventional or direct filtration; always < 1 NTU.
  ≤ 1 NTU (95% of the time) for slow sand, cartridge, and membrane; always < 5 NTU.

## Slide 13: Optimize Particle Removal
Optimize treatment for pathogen removal by optimizing particle removal (i.e., turbidity)

## Slide 14: Source water conditions can affect turbidity/pathogens
Watershed control
Intake structure or configuration & pumping facilities
Other factors affecting water quality (harmful algal blooms, point- and non-point source pollution, storms, runoff, etc.)

## Slide 15: Watershed Control
Owned or managed by the water system?
  Most systems have little control over their watersheds.
Drinking water protection plan
Emergency response plan
Patrols, gates, etc.
Inter-agency agreements (USFS, BLM, ODF, COE)
The Willamette River Basin is the largest watershed in the state, covering more than 11,500 square miles.

## Slide 16: Intakes and Pumps
Screens:
  well screens,
  traveling screens,
  self-cleaning rotating drum screens.
  Cleaned with air or water blast
Submersible pumps in slotted or perforated pipe laid on riverbed.

## Slide 17: Intakes and Pumps
Infiltration galleries: Slotted pipes or well screens underneath riverbed, provides rough filtration.
Vertical turbine pumps in wet wells are common in larger systems.

## Slide 18: Other Factors
Logging, wildfire, and storm events increase turbidity
Recreation (gasoline engines, oil)
Development (increased stormwater drainage with associated pollutants)
Seasonal and/or daily fluctuations in temp or pH
Harmful algal blooms (cyanobacteria) becoming an increasing problem
Sewage treatment plants upstream, occasional overflows
                2020 Wildfire Damage
                in Detroit, OR watershed
August 23, 2023 - Willamette Week article on HABs in Willamette R.

## Slide 19: FILTRATION

## Slide 20: Straining
Passing the water through a filter in which the pores are smaller than the particles to be removed

## Slide 21: Adsorption
The gathering of gas, liquid, or dissolved solids onto the surface of another material

## Slide 22: Types of Filtration
Conventional & Direct Filtration
Diatomaceous earth (DE, only a few in Oregon)
Slow Sand
Alternative (cartridge, bag & membrane)

## Slide 23: Conventional & Direct Filtration “Rapid Rate Filtration”

## Slide 24: Rapid Sand Filtration
Involves adsorption and physical straining of flocculated particles.
Mixed media filters: layers of support gravel, sand, anthracite.
Requires coagulation for charge neutralization, rapid mix (e.g., static mixer), and some degree of flocculation (e.g., large paddle wheel flocculator).
Filtration rate 2-4 gpm/ft2
Requires controllable backwash with water and perhaps air scour to clean filters.

## Slide 25: Media
Water flows through progressively larger pores as it passes from coal to sand to gravel.
This example shows the following from top to bottom (as the water would flow)
Anthracite
2 layers of sand
3 layers of support gravels
“Block” underdrain

## Slide 26: Conventional (and direct) filtration filter box
Perforated Pipe Underdrains

## Slide 27
Rapid sand filter
Notes: City of Forest Grove - CF

## Slide 28
Backwash of filter
Notes: City of Forest Grove - backwash

## Slide 29: Direct Filtration Lacks Sedimentation
  Direct Filtration Treatment
  “means a series of processes including coagulation (requiring the use of a primary coagulant and rapid mix) and filtration but excluding sedimentation resulting in substantial particulate removal.”

## Slide 30: Conventional Filtration
  In conventional filtration treatment..
    A coagulation chemical is added and rapidly mixed to neutralize particle charges
    Flocculation is a stage of gentle mixing so that a larger settleable floc forms
    Sedimentation is the stage were floc particles settle out prior to filtration

## Slide 31: Conventional Filtration
Sedimentation allows settling of coagulated particles, relieves burden on filter.

## Slide 32: Coagulants
Aluminum sulfate (alum): very common, only effective in narrow pH range.
Ferric chloride: More expensive, but works in wider pH range.
Poly aluminum chloride (PACL): not affected by pH, doesn’t change pH, works well with low alkalinity, leaves less sludge because dosage is low.
Aluminum Chlorohydrate (ACH): similar to PACL.

## Slide 33: Factors Affecting Coagulation
Dosage: determined by jar test for optimum qualities of floc: (size, settling rate).
Mixing: Mechanical or static. Need to rapidly mix chemicals.
Alkalinity: 50 mg/l or less can shift pH downward.
Temperature: Colder water slows coagulation.
Color: Pre-oxidation may be required.
Turbidity: Changing conditions require more frequent jar tests.

## Slide 34: Coagulation Depends on Rapid Mixing
Static mixers have veins or “elements” that promote mixing.
The more water is pushed through a static mixer, the higher the head loss and better mixing you have.

## Slide 35: Jar testing is used to optimize coagulant dose for the best floc formation
5 mg/L
Coagulant Dose
1 mL
10 mg/L
2 mL
15 mg/L
3 mL
20 mg/L
4 mL
25 mg/L
5 mL
30 mg/L
6 mL
Current Plant Dose

## Slide 36: Jar Testing Equipment
Jar Tester (6 jars, 300-rpm)
Six 2-L Square Jars
Portable or benchtop turbidimeter
pH analyzer
Misc. lab ware for making coagulant stock solution

## Slide 37: Flocculation
Flocculation involves slower mixing to bring neutralized particles together to form larger particles (floc)
Flocculation paddles - photo from 2007 CPE at Sweethome, OR

## Slide 38
Jar Test showing floc formation

## Slide 39: Sedimentation (Conventional Plants)
Standard basin:
  Usually rectangular, goal is to slow down the water so solids settle to bottom by gravity.
  Settled (clarified) water moves to filters slowly.
Tube settlers:
  Add capacity
  Solids only need to settle a few inches
  Water flows up through tubes, solids collect on the side and slide out of the bottom
  Some standard sed basins can be retrofitted with tube settlers
Plate Settlers (Lamella Plates)
  Perform same function as tube settlers
  Not as common in Oregon as tube settlers

## Slide 40: Sedimentation Basins
Sizing is such that the flocculated particles have time to settle out to the bottom of the basin before reaching the filters.
Flocculation > Sedimentation > Filtration
Settling
Distance
Less settleable particles will need to be removed by the filters

## Slide 41: Tube Settlers
City of Sweet Home, 2015
Tube settlers decrease the distance floc particles have to travel as they settle out.
In conventional basins, particles settle as much as 5-ft.
As water travel up through the inclined tube settlers, particles only settle about 2” to the floor of the tube.
Tubes decrease settling distance

## Slide 42: Inclined parallel plates serve a similar purpose as tube settlers
City of Corvallis, 2006
Plates also decrease the distance particles need to fall when settling out
Plates also decrease settling distance

## Slide 43: Adsorption (Upflow) Clarifiers
Coagulated water flows up through clarifier.
Clarifier media either gravel or plastic beads. Clarifier is periodically “rinsed” of solids.
Clarified water flows onto filter.
Configured as a package plant, small footprint, easy to increase the capacity.

## Slide 44: Contact Adsorption Clarifier
Roberts Filter Group Pacer II (model P-1400) ContaClarifierTM

## Slide 45
Upflow clarifier. Note screens (upper portion) holding clarifier gravel or plastic beads in place.

## Slide 46: Other Forms of Sedimentation
Other forms of sedimentation/clarification include:
  Solids contact clarifiers
  Sludge blanket clarifiers
  Dissolved air flotation
  Sand ballasted

## Slide 47: Direct Filtration
No sedimentation process.
OK for small systems with consistent raw water quality.
May be gravity or pressure filtration.
Usually cannot observe backwash process if pressure filtration.

## Slide 48
Pressure filters

## Slide 49: Conventional/Direct Filtration Optimization Objectives
Achieve filtration performance goals.
Minimize turbidity spikes during routine filter operation.
Minimize turbidity spikes following filter backwash.

## Slide 50: Optimization Goals for Conventional/Direct Filtration
Practice should embrace the multiple barrier approach
Adopt optimized performance goals
  (e.g., settled water turbidity < 1 NTU, filtered water turbidity < 0.1 NTU)

## Slide 51: Diatomaceous Earth (DE) Filtration

## Slide 52: Diatomaceous Earth (DE)
Common in swimming pools, also approved for drinking water.
Fine, porous, angular media processed from fossil skeletons of microscopic diatoms.
Requires a continuous “body feed” injection of DE, which collects on a filter screen (“septum”).
Only a few DE systems in Oregon.

## Slide 53
DE filter stack

## Slide 54
DE cake (pink layer)
Sediment that’s been filtered out (brown layer)

## Slide 55
DE cake
Sediment removed

## Slide 56
DE

## Slide 57: Slow Sand Filtration
Filtration rate < 0.1 gpm/ft2
Need raw water < 5 NTU
No coagulants used
Pathogen removal occurs due to biochemical processes and adsorption.
Cleaned by raking, and eventually removing, top 1/8” to ½” of sand.
Credited with 2.0-log Giardia/Crypto removal

## Slide 58: Slow Sand Filtration

## Slide 59
In a typical slow sand filter, water passes first through about 36 inches of sand, then through a layer of gravel, before entering the underdrain.
The sand removes particles from the water through adsorption, straining, and biological/biochemical processes.
A layer of dirt, debris, and microorganisms builds up on the top of the sand.
This layer is known as schmutzdecke, which is German for “dirt blanket“
The schmutzdecke breaks down organic particles in the water biologically and is also very effective in straining out even very small inorganic particles from water.

## Slide 60
Bird’s eye view of 4 large slow sand filter cells

## Slide 61
Large slow sand filter bed

## Slide 62
slow sand filter - drained

## Slide 63
Slow sand filters – 3 bays

## Slide 64: Slow Sand Filtration - Cleaning
Cleaned by scraping (manually with shovels or with a specially designed machine), and eventually removing schmutzdecke and top 1/8” to ½” of sand.

## Slide 65
Slow sand: left filter in service, right filter out of service

## Slide 66: Slow Sand Filtration - Cleaning
Some filters are designed to be “wet harrowed”

## Slide 67
Self-contained slow sand filters at a school designed for wet harrowing.

## Slide 68: Alternative Filtration Technologies
Cartridge / Bag Filters
Membranes
Need approved models that have met challenge studies (third party verification of performance) or on-site pilot data.

## Slide 69: Cartridge & Bag Filtration

## Slide 70: Cartridge Filters
Good for small systems with low flow rates (5-20 gpm).
Some cartridges require a specific pre-filter.
No backwash, cartridges are replaced when pressure differential reaches specified limit.
Must pass a challenge study in order to be approved.

## Slide 71
The state maintains a list of approved cartridge units on its website
Operational boundaries (max flow, max pressure drop) associated w/ approval & log removal credit

## Slide 72
Cartridge housings in sequence

## Slide 73
Cartridge housings in parallel

## Slide 74
Another style of cartridge housings

## Slide 75
Filter cartridges that go in the housings

## Slide 76
Bag filter

## Slide 77: Membrane Filtration

## Slide 78: Membrane Filtration
Remove pathogens based on pore size
Typically consist of bundles of hollow fibers.

## Slide 79
Fibers can have different wall thicknesses and configurations
Asahi Kasei Microza™ UNA-620A MF fibers
Innovative Membrane Technologies (IMT) SevenBore® UF Fiber
Asahi Kasei Microza™ UNA-620A MF fibers in potting resin

## Slide 80: Membrane Filtration
Can be in pressurized modules

## Slide 81
Pressurized membranes

## Slide 82
Large membrane plant.

## Slide 83
Membranes (pressure)

## Slide 84: Membrane Filtration
May also be submerged in basins

## Slide 85
Plant with submerged membranes

## Slide 86
Submerged membrane racks
Notes: .

## Slide 87
Membrane backwash, submerged membranes

## Slide 88: Membrane Filtration
Very small pore sizes, 1 micron or less

## Slide 89: Membrane Filtration
Often need pre-filter/screening (30 – 300 micron screens)
May also need coagulant to remove soluble organics

## Slide 90: Membrane Filtration
Requires direct integrity test daily (usually air-hold pressure decay testing which is pre-programmed into automated controls).

## Slide 91: Membrane Filtration
Holes in the membrane fibers or broken fibers result in a measurable pressure drop during direct integrity testing as shown by the air bubbles in site tubes.

## Slide 92
Membrane Filtration
Control panel showing DIT (pressure decay test) info:
DIT= direct integrity test - sometimes called membrane integrity test (MIT),
pressure decay test (PDT), or air hold test.
LRV=log removal value

## Slide 93
Damaged or broken membrane fibers can be “pinned” (plugged).
Membrane Filtration

## Slide 94
Membrane clean-in-place chemicals
Membrane Filtration
Membranes are periodically cleaned with acid, caustic, and/or chlorine.

## Slide 95
The state maintains a list of approved membrane units on its website
Approved under certain operating conditions (max flow, test pressures)
Membrane Filtration

## Slide 96: Different methods of filter cleaning:
Conventional/Direct Filtration
  Backwashing (every 8 – 72 hours)
  Replacing/adding media eventually
Slow sand
  Scraping/ripening (every 1 – 6 months)
  Replacing/adding sand eventually
Cartridge/bag
  Discard/replace used filters
Membrane
  Backwash (every 60 – 90 minutes)
  Chemical cleaning

## Slide 97: 15 Minute Break

## Slide 98: 15 Minute Break
10 minutes left

## Slide 99: 15 Minute Break
5 minutes left

## Slide 100: Disinfection
For this section on disinfection, you will need Exercise Handouts #1 - #3 found at the link posted in the chat window on the right.

## Slide 101: Disinfection Overview
What is disinfection?
Types of disinfectants
Forms of chlorine
NSF/ANSI Standard 60
Disinfection requirements for surface water
CTs
Tracer Studies and Contact Time
Impact of disinfectants on organics

## Slide 102: What is disinfection?
Process of killing microorganisms in water that might cause disease (pathogens)
Should not be confused with sterilization which is the destruction of all microorganisms
Two types:
  Ultraviolet Light (UV) Radiation
  Chemical (chlorine, chloramines, chlorine dioxide, ozone)

## Slide 103: Ultraviolet Light (UV)
Works by subjecting water to ultraviolet (UV) light rays as water passes through a tube
https://www.unh.edu/wttac/WTTAC_Water_Tech_Guide_Vol2/uv_homepage.html

## Slide 104
Quartz UV bulb sleeve

## Slide 105
UV reactors at a large water system

## Slide 106: The state maintains a list of approved UV units on its website
NSF 55 units not allowed for SW treatment (only allowed for GW TC+ with small distribution)

## Slide 107: UV Drawbacks
Drawbacks for UV include:
  Interfering agents such as turbidity can screen pathogens from the UV light
  Effective against Giardia and Cryptosporidium but not viruses at normal doses
  No residual is present in the water to continue disinfecting throughout the distribution system
  For this reason, chlorination for residual maintenance is required when UV is used

## Slide 108: Chemical Disinfection
Chlorine
Chloramines
Chlorine dioxide
Ozone

## Slide 109: Chlorine
Most widely used form of disinfection
Also used as an oxidizing agent for iron, manganese and hydrogen sulfide and for controlling taste and odors
Effectiveness as a disinfecting agent depends on factors such as pH, temperature, free chlorine residual, contact time and other interfering agents

## Slide 110: Forms of Chlorine
Sodium Hypochorite
Onsite generated sodium hypochorite
Calcium Hypochlorite
Chlorine Gas

## Slide 111: Sodium hypochlorite
The liquid form of chlorine
Clear and has a slight yellow color
Ordinary household bleach (~5% chlorine by solution) is the most common form
Industrial strength: 12% and 15% solutions

## Slide 112: Sodium hypochlorite (continued)
Can lose up to 4% of its available chlorine content per month; should not be stored for more than 60 to 90 days
Very corrosive; should be stored and mixed away from equipment that can be damaged by corrosion

## Slide 113: Diaphragm Pump/Tank for Chlorine

## Slide 114: On-site generated sodium hypochlorite
0.8% sodium hypochlorite is produced on demand by combining salt, water & electricity
Electrolysis of brine solution produces sodium hydroxide and chlorine gas, which then mix to form sodium hypochlorite
Hydrogen gas byproduct; vented to atmosphere
Alleviates safety concerns associated w/ hauling and storing bulk chlorine
Higher initial cost, high power cost
Mixed oxidants (proprietary)

## Slide 115
Electrodes for onsite chlorine generation

## Slide 116: Calcium hypochlorite
The solid form of chlorine
Usually tablet or powder form
Contains ~65% chlorine by weight
White or yellowish-white granular material and is fairly soluble in water
Important to keep in a dry, cool place
More stable than liquid
Used by small systems w/ low flows or no power

## Slide 117
Calcium hypochlorite erosion feeder

## Slide 118: Calcium hypochlorite hopper interior
Notes: Cal hypo erosion feeder

## Slide 119: Chlorine gas (Cl2)
99.5% pure chlorine
yellow-green color 2.5x heavier than air
Liquified at room temperature at ~107 psi – hence the pressurized cylinders actually contain liquified chlorine gas.
Liquified Cl2 is released from tanks as chlorine gas, which is then injected into the water stream.
usually used only by large water systems
Smaller systems may find initial cost of operation prohibitive

## Slide 120
1-ton chlorine gas cylinders

## Slide 121
1-ton chlorine gas cylinders
Note: scales used to weigh cylinders (to tell when they are empty)
Notes: 1-ton cl2 gas cylinders

## Slide 122
150-lbs chlorine gas cylinders
Chain to secure tank in place
Spare tank on hand
Tanks clearly marked

## Slide 123: Chloramines
Chlorine + ammonia = chloramination
Two advantages to regular chlorination:
  produce a longer lasting chlorine residual (helpful to systems with extensive distribution systems)
  may produce fewer by-products depending on the application
Disadvantage:
  Need a lot of contact time to achieve CTs compared to free chlorine (300 times more) which is why not used for primary disinfection
  Requires specific ratio of chlorine to ammonia or else potential water quality problems

## Slide 124
Ammonia for making chloramines

## Slide 125: Ozone
Colorless gas (O3)
Strongest of the common disinfecting agents
Also used for control of taste and odor
Extremely Unstable; Must be generated on-site
Manufactured by passing air or oxygen through two electrodes with high, alternating potential difference

## Slide 126
Large water system ozone
Notes: Ozone reactors Reedsport

## Slide 127
Large water system ozone
Notes: Ozone reactor Medford

## Slide 128
Ozone contactors

## Slide 129
Ozone is to reactive to store, so liquid oxygen is used for making ozone

## Slide 130: Ozone advantages
Short reaction time enables microbes (including viruses) to be killed within a few seconds
Removes color, taste, and odor causing compounds
Oxidizes iron and manganese
Destroys some algal toxins
Does not produce halogenated DBPs

## Slide 131: Ozone disadvantages
Overfeed or leak can be dangerous
Cost is high compared with chlorination
Installation can be complicated
Ozone-destroying device is needed at the exhaust of the ozone-reactor to prevent smog-producing gas from entering the atmosphere and fire hazards

## Slide 132: Ozone disadvantages (continued)
May produce undesirable brominated byproducts in source waters containing bromide
No residual effect is present in the distribution system, thus postchlorination is required
Much less soluble in water than chlorine; thus special mixing devices are necessary

## Slide 133: Chlorine dioxide
Advantages
More effective than chlorine and chloramines for inactivation of viruses, Cryptosporidium, and Giardia
Oxidizes iron, manganese, and sulfides
May enhance the clarification process
Controls T&O resulting from algae and decaying vegetation, as well as phenolic compounds
Under proper generation conditions halogen-substituted DBPs are not formed
Easy to generate
Provides residual
Notes: From: EPA Guidance Manual Alternative Disinfectants and Oxidants, April 1999

## Slide 134: Chlorine dioxide (continued)
Disadvantages
Forms the DBP chlorite
Costs associated with training, sampling, and laboratory testing for chlorite and chlorate are high
Equipment is typically rented, and the cost of the sodium chlorite is high
Explosive, so it must be generated on-site
Decomposes in sunlight
Can lead to production noxious odors in some systems.

## Slide 135: NSF/ANSI Standard 60
Addresses the health effects implications of treatment chemicals and related impurities.
The two principal questions addressed are:
  Is the chemical safe at the maximum dose, and
  Are impurities below the maximum acceptable levels?

## Slide 136
NSF approved sodium hypochlorite

## Slide 137: Disinfection Requirements for Surface Water
Surface Water Treatment Rule (SWTR) requires 3-log reduction of Giardia using a combination of disinfection and filtration
2.0 to 2.5-log removal is achieved through filtration
0.5 to 1.0-log inactivation is achieved through disinfection
Determines which column of EPA tables used to calculate CTs (0.5 or 1.0-log)

## Slide 138: What are CT’s?
It’s a way to determine if disinfection is adequate
CT = Chlorine Concentration x Contact Time
Do not confuse “CT” and “Contact Time”
Notes: C stands for concentration (not chlorine) which explains how CT can also be used for ozone, UV, etc.

## Slide 139: How do we calculate CT’s?
We use the EPA tables to determine the CTs needed to inactivate Giardia (CTrequired)
  We need to know pH, temperature, and free chlorine residual at the first user in order to use the EPA tables.
Then we compare that with the CTs achieved in our water system (CTactual)
CTactual must be equal to or greater than CTrequired

## Slide 140: Tracer Studies and Contact Time:
Used to determine contact time (T) which is used in calculating CT’s
Determines the time that chlorine is in contact with the water from the point of injection to the point where it is measured (sometimes referred to as the “CT segment”)
    May be at or before the 1st user
    May be more than one CT segment
Estimates of contact time are not allowed for calculating CT’s for surface water!
  The degree of short-circuiting is only approximately known until a tracer study is conducted.
Notes: OAR 333-061-0050(6):
(R) Reservoirs and clearwells that are to be used for disinfection contact
time to treat surface water shall use a tracer study to determine the
actual contact time. The Department must approve procedures and
protocols for the tracer study prior to the initiation of the study. The
Department recommends the USEPA SWTR Guidance Manual for
tracer study procedure and protocol.
(S) Reservoirs and clearwells that are to be used for disinfection contact
time to treat surface water shall have a means to adequately determine
the flow rate on the effluent line.
OAR 333-061-0036(5) says that the disinfectant contact time T must be determined each day during peak hourly flow, based on results of a tracer study or other method approved by the Department.

## Slide 141
What effects short-circuiting?
Flow rate
Flow path

## Slide 144
The CT segment is from where chlorine is added here:

## Slide 145
Thru the clearwell, to where chlorine residual is measured here:

## Slide 146
So if we were conducting a tracer study, this is the segment we would be looking at and determining the contact time T for.

## Slide 147: Tracer studies (continued):
Different methods:
  If water is pumped from the clearwell at different rates depending on time of year, do tracer study at each of those flow rates
  Do at typical winter/summer peak hour demand flows
  Otherwise use “worst-case scenario” parameters:
    Highest flow rate out of clearwell (conduct during peak hour or conditions that simulate e.g. open a hydrant)
    Keep flow rate constant
    Keep clearwell water level close to normal minimum operating level

## Slide 148: Tracer studies (continued):
Must redo if peak hour demand flow increases more than 10% of the maximum flow used during the tracer study
Community water systems with populations <10,000 and non-profit non-community systems can use the circuit rider to perform a tracer study
Must submit a proposal to DWS for approval prior to conducting the tracer study (even if using the circuit rider).

## Slide 149: Exercise #1
Tracer studies

## Slide 150
Exercise #1: Tracer studies
Directions: Look at the diagram and answer the questions.
Figure 1: Water Treatment Plant
Smith Creek
Slow sand filter #1
Slow sand filter #2
Reservoir
75,000 gal.
Clearwell 220,000 gal
Chlorine injection
To distribution
NTU, flow
NTU
NTU
Flow
16.1’ max volume
10.5’ min volume
Flow control valve: 270 gpm max
Two houses
Questions:
If this was your treatment plant, highlight the part of the plant where you might conduct a tracer study.
In a “worst-case scenario” tracer study, what would the flow rate be?
In a “worst-case scenario” tracer study, what would the clearwell level be?

## Slide 151
Exercise #1: Tracer studies
Directions: Look at the diagram and answer the questions.
Figure 1: Water Treatment Plant
Smith Creek
Slow sand filter #1
Slow sand filter #2
Reservoir
75,000 gal.
Clearwell 220,000 gal
Chlorine injection
To distribution
NTU, flow
NTU
NTU
Flow
16.1’ max volume
10.5’ min volume
Flow control valve: 270 gpm max
Two houses
Questions:
If this was your treatment plant, highlight the part of the plant where you might conduct a tracer study.
In a “worst-case scenario” tracer study, what would the flow rate be?
In a “worst-case scenario” tracer study, what would the clearwell level be?
Notes: Mute presenter for 2 minutes

## Slide 152
Exercise #1: Tracer studies
Directions: Look at the diagram and answer the questions.
Figure 1: Water Treatment Plant
Smith Creek
Slow sand filter #1
Slow sand filter #2
Reservoir
75,000 gal.
Clearwell 220,000 gal
Chlorine injection
To distribution
NTU, flow
NTU
NTU
Flow
16.1’ max volume
10.5’ min volume
Flow control valve: 270 gpm max
Two houses
Questions:
If this was your treatment plant, highlight the part of the plant where you might conduct a tracer study.
In a “worst-case scenario” tracer study, what would the flow rate be? 270 gpm
In a “worst-case scenario” tracer study, what would the clearwell level be? 10.5 feet

## Slide 153: How info from tracer study is used to calculate CTs
Use the time T from the tracer study on the monthly reporting form in the “Contact time (min)” column
  Use the smallest T (highest flow) if the tracer study was done at multiple flow rates
This may not be your exact time, but it represents your worst case (as long as the peak flow is less and clearwell volume is more than they were at the time of the tracer study)

## Slide 154: How info from tracer study is used to calculate CTs (cont.)
Or, once you know the time T from the tracer study, you can back-calculate to determine the baffling factor of the clearwell
    Baffling factor (%) = Time (min) x Flow During Tracer Study (gpm)
Clearwell Volume During Tracer Study (gal)
T can be adjusted based on flow (at <110%) with the following equation:
    T = Current clearwell Volume (gal) x Baffling Factor (%)
    Peak Hourly Demand Flow (gpm)
If tracer study includes pipeline segments or multiple tanks, contact the state for guidance on using baffling factors
Notes: You can go 10% above what it was during the tracer study.

## Slide 155: Impact of chlorine and ozone on organics
Disinfectants can react with organics to form disinfection byproducts
  Chlorine: TTHMs & HAA5s
  Ozone: Bromate
Pre-chlorination
TOC

## Slide 156: OPERATIONS

## Slide 157: Overview
Proper instrument sampling locations
Proper treatment plant sampling locations
  Turbidity
  Chlorine residual
  TOC
Instrument calibration
  Turbidimeters
  Chlorine analyzers
  Chemical feed pumps
Operations & Maintenance Manuals

## Slide 158: Proper instrument sampling location
Data provided by instruments provides the basis for assessing water quality – important to get it right!
Common problems
  Sampling location
  Measurement techniques
  Calibration frequency and approach
Possible solutions
  May require investigations (special studies)
  Modifications to sample lines
  Establish guidelines on sample line cleaning
  Establish calibration procedure

## Slide 159: Sampling for Turbidity
Raw turbidity
  Applies to all SW systems
  Location: pre-treatment
  Frequency: no regulatory requirement but need to know for proper treatment plant operation
  Settled turbidity
  Water systems using conventional filtration must measure settled water turbidity every day (e.g., grab sample 1x/day).
Individual filter effluent (IFE) turbidity
  CF, DF & membranes only
  Location: after each individual filter
  Frequency: continuous (every 15 minutes)
  Know what the triggers are!

## Slide 160: IFE Triggers (Conventional/Direct)
  Report the following events immediately and conduct a filter profile within 7 days (if no obvious reason exists) if the IFE turbidity is:
    > 1.0 NTU in 2 consecutive 15-min readings
    > 0.5 NTU in 2 consecutive 15-min readings within 4 hours of being backwashed or taken off-line
  Report the following events and conduct a filter self assessment within 14 days if the IFE turbidity is:
    > 1.0 NTU in 2 consecutive 15-min readings at any time in each of 2 consecutive months.
  A CPE must be done within 30 days if the IFE turbidity is:
    > 2.0 NTU in 2 consecutive 15-min readings at any time in each of 2 consecutive months.

## Slide 161: Proper treatment plant sampling locations: Turbidity (cont.)
Combined filter effluent (CFE) turbidity
  Applies to all SW systems
  Location: post all filtration prior to chemical addition and any storage
  Frequency:
    CF/DF > 3,300 pop. – continuous
    CF/DF ≤ 3,300 pop. – every 4 hrs
    Alternative - daily

## Slide 162: Proper treatment plant sampling locations: Chlorine residual
Must be at least 0.2 ppm all times at the entry point (EP) to the system
  EP = post clearwell, at or before 1st user
EP chlorine residual sampling frequency
  Continuous > 3,300 population
  1-4x/day for ≤ 3,300 population
If EP residual falls < 0.2 ppm or required continuous monitoring equipment fails, grab sampling must be done every 4 hours until the residual is > 0.2 ppm and/or equipment is repaired.

## Slide 163: Proper treatment plant sampling locations: Chlorine residual
OAR 333-061-0032(5)

## Slide 164: Proper treatment plant sampling locations: Chlorine residual
OAR 333-061-0036(5)(b)(D)
Note - OAR 333-061-0036(5)(b) – addresses monitoring for SW and GWUDI systems that provide filtration. Section -0036(5)(a) is for unfiltered systems, but the disinfectant residual monitoring under (5)(a)(E) still applies.

## Slide 165: Proper treatment plant sampling locations: Chlorine residual
OAR 333-061-0036(5)(a)(E) – EP Chlorine Residual

## Slide 166: Proper treatment plant sampling locations: Total organic carbon (TOC)
Applicability
  CF (2.5-log plants): required raw TOC & alkalinity and filtered TOC
  All others: raw TOC required to qualify for DBP monitoring reduction (>500 population)
Frequency
  Monthly; may be reduced to Quarterly if filtered TOC is <2.0 ppm for 2 years, or <1.0 ppm for 1 year
  Quarterly if DBP reduction is granted

## Slide 167: Proper treatment plant sampling locations: Total organic carbon (TOC) (cont.)
Location
  Raw TOC & alkalinity: pre-treatment
  Filtered TOC: CFE prior to chemical addition/disinfection
    <2.0 ppm for 2 years, or
    <1.0 ppm for 1 year
Coagulant
Chlorine

## Slide 168: Exercise #2
Proper sampling locations for turbidity, chlorine residual, and TOC
  Determine proper sampling locations on WTP diagrams for conventional and membrane filtration

## Slide 169
Conventional Filtration >
Notes: Mute presenter for 2 minutes

## Slide 170
Settled water turbidity
(required for conventional filtration plants only)
Conventional Filtration >

## Slide 171
Membrane Filtration>

## Slide 172
Membrane Filtration>
Raw water TOC if seeking DBP sampling reduction.
Paired post-filtration TOC is recommended to evaluate organics removal and/or demonstrate impact of coagulation

## Slide 173: Instrument calibration
Turbidimeters (online, portable or benchtop)
  Must be calibrated per manufacturer or at least quarterly with a primary standard
    Formazin solution
    Stablcal (stabilized formazin)
  Secondary standards used for day-to-day check
  dayCheck is used to determine if calibration with a primary standard is necessary
    Gelex
    Manufacturer provided (e.g. Hach ICE-PIC)

## Slide 174
Portable turbidimeter

## Slide 175: Instrument calibration
Chlorine analyzers
  Handheld
    Follow manufacturer’s instructions
  Inline
    Check calibration against a handheld that has been calibrated
    At least weekly
    Follow manufacturer’s instructions if out of calibration

## Slide 176
Portable colorimeter

## Slide 177: Instrument calibration
Chemical feed pumps
  Calibration measures both the speed and the stroke (amount of chemical pumped) so accurate dosages can be calculated
  Create a “pump curve”;
    Set the stroke at half way point
    On a graph, plot speeds of 10% to 100% on X axis
    Plot chemical output amount on Y axis (ml/min)
    Record drawdown in graduated cylinders for 1 minute

## Slide 179: Instrument calibration (cont.)
Chemical feed pumps (cont.)
  Pump curve is an important tool to identify when a pump may be in need of maintenance or replacement
  A smooth pump curve is good (should fit close to a straight line)
  Must compare information at varying speeds to be a full pump calibration process
  Suggested frequency: no less than annual

## Slide 180
Chemical feed pumps

## Slide 181: Exercise #3
Create a pump curve using made-up data points
Directions: Use the data provided in Exercise #3 to create a pump curve. Pump curves should be smooth and fairly linear. A bouncing or jagged pump curve indicates the pump needs maintenance. Maintenance needed may include cleaning, diaphragm replacement and/or seal replacement.
Notes: Mute presenter for 2 minutes

## Slide 182
Exercise #3: Creating a chemical feed pump curve
Directions: Use the data provided in the examples below to create a pump curve. Pump curves should be smooth and fairly linear. A bouncing or jagged pump curve indicates the pump needs maintenance. Maintenance needed may include cleaning, diaphragm replacement and/or seal replacement.
Feed pump #1 pump curve data:
Plot the data points on the graph. Does the pump need maintenance?
Setting | Time | Volume | Flow Rate
% Speed | Minutes | ml | ml/min
10% | 3 | 60 | 20
20% | 3 | 360 | 120
30% | 3 | 420 | 140
40% | 3 | 810 | 270
50% | 3 | 900 | 300
60% | 1 | 450 | 450
70% | 1 | 400 | 400
80% | 1 | 525 | 525
90% | 1 | 530 | 530
100% | 1 | 575 | 575

## Slide 183
Exercise #3: Creating a chemical feed pump curve
Directions: Use the data provided in the examples below to create a pump curve. Pump curves should be smooth and fairly linear. A bouncing or jagged pump curve indicates the pump needs maintenance. Maintenance needed may include cleaning, diaphragm replacement and/or seal replacement.
Feed pump #1 pump curve data:
Plot the data points on the graph. Does the pump need maintenance? Yes (jagged line)
Setting | Time | Volume | Flow Rate
% Speed | Minutes | ml | ml/min
10% | 3 | 60 | 20
20% | 3 | 360 | 120
30% | 3 | 420 | 140
40% | 3 | 810 | 270
50% | 3 | 900 | 300
60% | 1 | 450 | 450
70% | 1 | 400 | 400
80% | 1 | 525 | 525
90% | 1 | 530 | 530
100% | 1 | 575 | 575

## Slide 184
Feed pump #2 pump curve data:
Plot the data points on the graph. Does the pump need maintenance? No (straight-ish, smooth line)
Setting | Time | Volume | Flow Rate
% Speed | Minutes | ml | ml/min
10% | 3 | 120 | 40
20% | 3 | 270 | 90
30% | 3 | 480 | 160
40% | 3 | 690 | 230
50% | 3 | 960 | 320
60% | 1 | 400 | 400
70% | 1 | 460 | 460
80% | 1 | 500 | 500
90% | 1 | 540 | 540
100% | 1 | 560 | 560

## Slide 185
Bonus question: Referring to feed pump #2 data above, if you normally have your speed set at 50% in order to maintain 1 ppm of chemical, what speed do you need to change it to if you do a new pump curve and get the following results:
Feed pump #2 NEW pump curve data
Answer: 60%
Setting | Time | Volume | Flow Rate
% Speed | Minutes | ml | ml/min
10% | 3 | 60 | 20
20% | 3 | 120 | 40
30% | 3 | 270 | 90
40% | 3 | 480 | 160
50% | 3 | 690 | 230
60% | 1 | 320 | 320
70% | 1 | 400 | 400
80% | 1 | 460 | 460
90% | 1 | 500 | 500
100% | 1 | 540 | 540

## Slide 186: Lessons learned from data assessments done in the past
Common findings:
  Most systems have some problems with the way they monitor, record, assemble, and/or report data
  Operators do not know which data to report and which to exclude
  Operators do not know how to correctly use their tracer studies/calculate CTs
  Most system managers and operators are surprised by what they find out from a data assessment

## Slide 187: Data assessments (cont.)
Even automated systems require a knowledgeable person to correctly assemble data
Data assessments often used to justify invalidation of turbidity data which would have triggered a CPE
Effective optimization can only be achieved when using valid performance data

## Slide 188: How can operators become better data managers?
Make data reliability a plant goal
Only collect data used for process control or compliance reporting
Establish protocols for collection and recording of data
Establish a data verification process that can be routinely used to confirm data integrity
Turn data into information!

## Slide 189: Operations & Maintenance Manual
Keep written procedures on:
Instrument calibration methods and frequency
Data handling/reporting
Chemical dosage determinations
Filter operation and cleaning
CT determinations
Responding to abnormal conditions (emergency response plan)

## Slide 190: End of Part 1
Attend Part 2 to receive an additional 3 Contact Hours.
Complete the application for both parts attended to get all 6 contact hours online at: https://www.oregon.gov/oha/PH/HEALTHYENVIRONMENTS/DRINKINGWATER/OPERATIONS/TREATMENT/Pages/sw-essentials.aspx
The link to attend Part 2 of the training and application for contact hours is online under “Free Training Resources” at www.healthoregon.org/swt
E-mail questions to: DWS.SurfaceWater@odhsoha.oregon.gov