## Slide 1: Oregon Health Authority Drinking Water Services
Oregon Association of Water Utilities
Notes: This presentation is a collaborative effort from Oregon Health Authority-Drinking Water Services and Oregon Association of Water Utilities to assist water personnel operating a community or non-transient non community water system.
Focus on those system that have a higher level of potential exposure (daily usage) to possible lead associated with service line components

## Slide 2: Service Line Inventories
Notes: Welcome public water personnel who are tasked with completing service line inventories., to confirm either the existence or non-existence of lead in the service lines.
Key take aways from this presentation will be a guided approach to completing service line inventories, acceptable procedures and resources of information.
This information is applicable to the course, but keep attentive to rule changes as the complexity of the rule encompasses the country as a whole

## Slide 3: Oregon’s Website for Lead Info
www.Oregon.gov/LCRR
Notes: Templates
  Available from the OHA-DWS, suggesting using the template – standard form
    Ease of use
  With the amount of information required, this State’s efforts support using the template
  Outlines the instructions for the spreadsheet, - descriptions, inventory sheet, replacement plan
    Consider using a tablet in the field to complete inventory

## Slide 4
Notes: Webpage has lots of information

## Slide 5: Key Points
Update to Lead and Copper Rule – 1991 Original – 68K PWS
Revisions in 2000 and 2007 (monitoring, treatment, etc.)
Major revision in 2021 – (SL inventory / replacement)
Inventory – ID all services lines for possible lead
Lead and Copper Rule Improvements – 2024 (LCRI)
Notes: PURPOSE ___ Minimizing Exposure to Lead by strengthening drinking water treatment standards for:
  corrosion control in systems
  removing sources of lead and
  educating consumers
2000 and 2007 revisions geared to WT – monitoring have reached 90 percent compliance
2021 the rule becomes more concise, transparent, with fewer discretionary judgments having the decision-making process more objective.
LCR – I improvement will better clarify by updating inventories.
  Change in tap sampling,
  Possibly lowering the MCL from 15 ppb to 10 ppb,
  exceedances require outreach to consumers, create filter program
Within ten years achieve 100% replacement of all discovered lead service lines

## Slide 6: Which Oregon PWSs are Affected
Community Water Systems – 900
Non-Transient Non-Community – 300
OAR – 333-061-0036 (10)
Transient Non-Community - NOT AFFECTED
Oregon Very Small – 4-14 connections – NOT AFFECTED
Notes: The level of exposure – how much of the public is exposed to water through normal daily routine
CWS, for obvious reasons have the highest level of potential exposure
The rule is noted on the slide if you wish to review – understand, it is two pages – 5 key points –
  Develop inventory
  Approved methodologies
  Categorization of services lines
  Updating of inventories
  Lead – Galvanized Required Replacement – UNK inventory updates as monitoring schedules for lead and copper sampling will be updated
The two classifications of water systems are noted at points 4 and 5 are not subject to the rule

## Slide 7: LCR Revisions - OREGON
333-061-0036(10)(h)(A)
  Effective February 2023
  Inventories – due to State October 16, 2024
Regulations for inventory work – is the focus
Base line inventory – annual update
Oregon finalization within 3 years of EPA rule making
Example of service line
Notes: LCRR – Oregon adopted by reference the EPA revisions of the rule 2021
  Key elements of Oregon rules October 2024
  FAQ found on the OHA_DWS webpage – updated October 2023 explains basic questions for inventories
Methods to perform inventory work
State adoption of from LCR improvement is yet TBD
Primacy is TBD as to when
Let’s look at a typical service line

## Slide 8
Responsibility of Water System
Responsibility of Water System
Notes: Quick depiction showing areas of responsibility
  Note line of demarcation more detail later in the presentation
  Water Purveyor
    EPA 3 pts of investigation suggested,
    Oregon 1 single point verbal input from homeowner + visual inspection close to the meter (Distance-?)
Congress mandates PWS must report to customer to obtain pipe material……reasonable effort
Obligated to identify both pipe materials – PWS side, customer side

## Slide 9
Notes: Quick depiction showing areas of responsibility
  Note line of demarcation more detail later in the presentation
  Water Purveyor
    EPA 3 pts of investigation suggested,
    Oregon 1 single point verbal input from homeowner + visual inspection close to the meter (Distance-?)
Congress mandates PWS must report to customer to obtain pipe material……reasonable effort
Obligated to identify both pipe materials – PWS side, customer side

## Slide 10: Oregon Lead Ban
July 1, 1985 – use of lead components banned
PWS pre-certification does not meet current regulations
Will help support current regulations
Verbal historical knowledge does not replace physical inspection
Will not meet LCRR – incorrect method
PWS side should not have any “known” lead components
January 1, 1986 – installations after considered NL
Notes: Historical information that will assist in determining SL probability
PWS will be required to investigate each service line regardless of previous information
  Exceptions are after January 1986 installations – documents must state type of pipe material
  Work orders after January 1986
Documentation to prove
Verbal information, contrarian ideas (public knowledge) may trump circumstantial evidence
No
Straightforward
Last bullet tells us a “physical: inspection, verification is mandated
  Well documented paperwork from past work can substantiate lead / no lead

## Slide 11: Service Line Inventory Requirements OAR -333-061-0036 (10)(h)(A)(i)
(A)(i) Water suppliers must develop an inventory to identify the lead status of all public and private service lines connected to the public water distribution system. The inventory must:
(I) Utilize evidence-based methodologies as listed in subparagraph (10)(h)(A)(ii) of this rule.
(II) Categorize each public and private service line as described in subparagraph (10)(h)(A)(iii) of this rule. Water suppliers are not required to physically verify the material composition (for example, copper or plastic) of a service line to identify its lead status in the inventory; and
(III) Be submitted to the Authority no later than October 16, 2024, in a format approved by the Authority
(State’s Spreadsheet)
Notes: (A)(i)Lead service line requirements –Identify –
  ID pipe material on both he PWS side and customer side
(I) Evidenced based on rule criteria
(II) Not required – physically, but categorized as LEAD / Galvanized Required Replacement / non-LEAD / UNK
(III) Approved format will discuss while looking at the excel spreadsheet

## Slide 12: Service Line Inventory Jargon -
Initial SL inventory completed (to the State) October 16, 2024 -
Lead Service Lines (LSL)
Galvanized Requiring Replacement (GRR)
Non-Lead (NL)
Unknown Service Lines (lead status) (UNK)
Notes: Just another reminder of the deadlines, recommend having info to the State by early September
Where the SL is made of lead – any component
It is or was downstream of Lead Service Lines or UNK
Non lead evidenced based record, classifying actual material, PVC, CPVC, Copper, PEX, Muni-PEX
Classifying UNKNOWNS
  Not known to be lead, Galvanized Required Replacement or non-lead and no evidence documented

## Slide 13: Unknowns
Initial Inventory
Service lines unverified, unsupported = Unknowns
Unknown lines must eventually be confirmed
Encourage to confirm all unknowns
Rules may change with LCR Improvements
  Expected to be released late 2024
Notes: Initial inventory completed and turned in by October 16, 2024
Note remaining time to complete survey
If proven no Lead Service Lines, the PWS task for Lead Service Line is complete
UNK – will have to be inspected and confirmed NO LEAD –it WILL be assumed some component contains LEAD
If service line is disturbed, notify customer.
Pertains more to the east coast, but if line is disturbed, flushing prior to consumption can reduce potential lead levels
  Per CFR To mitigate potential lead exposure associated with a partial SL replacement until the PWS completes a full replacement, the PWS must provide the consumer with a POU FILTER device with six months of replacement cartridges to consumers until the replacement is completed.
  Partial SL replacement, may contribute higher levels of lead into the drinking water,
    PWS must provide a filter within 24 hours of learning of the customer replacement that left a system owned SL in place within the past six months.
  PWS with full SL replacement must provide customer notification and risk mitigation before the service line is returned to service.
LCR Improvements (LCRI) are still being finalized , likely in effect in mid 2024

## Slide 14: Service Line Inventory
Lead connectors – (goosenecks or pig tails)
Not required to be included in inventory – not part of SL
Oregon recommends including lead connectors
Lead connectors must be replaced when found (Oregon law)
Notes: Per OAR
The final rule requires the replacement of the lead goosenecks, pigtails and connectors any time they are encountered by the water system.
  EPA does NOT consider these type of connectors to be PART of the SL
OAR 333-061-0036 (10)(h)(A)(i) (II) not required to physically verify the materials composition
Lead connectors, though rare in Oregon should be included in inventory
Law in effect since July 1,1985

## Slide 15: Galvanized Requiring Replacement
Gray is PWS
Light Blue is Customers
Dark Blue Classification

## Slide 16: Service Line Inventory – Galvanized
Galvanized Requiring Replacement – must ID location
If lead is found, make available to public along with UNK
Inventory updated annually
PWS on reduced monitoring – tri-annually
All service connections –
  Residential, commercial, irrigation, fire lines, etc.
Look at a flow chart showing galvanized
Notes: Must ID location – good time to begin info for future mapping
  Replacement if found to follow lead component previously or currently.
  No replacement if there was never a lead component up stream from the galvanized pipe.
  If lead cannot be confirmed to never exist, presumed upstream was lead
Make known to the public - homeowner (landlord),
Annually – until rules will clarify any change
Will follow the existing monitoring schedule for your system
EVERYTHING two inches or greater can be listed as non lead
If no lead is discovered, no new updates, equals a finished inventory

## Slide 17: Methodology
Taken from Service Line Material Journal
https://awwa.onlinelibrary.wiley.com/doi/epdf/10.1002/awwa.1841
Journal AWWA Volume 114, Issue 1
Published January 2022
Notes: We wanted to show a simple step process towards attainment
What does the paperwork say? Good documents will ease the process
Paperwork will scrutinize the components and categorize
Field investigation –
Compile the excel spreadsheet

## Slide 18: OAR -333-061-0036 (10)(h)(A)(ii)
(I) State approved methodologies
    Follow existing records
          Construction drawings, plumbing code,
          service line materials
          Distribution maps, meter install records,
(II) Installation after January 1, 1986 – non lead
Construction standards set prior to – non lead
(III) 2+ inches – non lead
(IV) Customer submittal of lead status at building
Notes: Per rule methodologies
PAPERWORK - Construction, plumbing codes, building permits, dates, system maps, etc.
Water system construction codes precede January 1986 –
Customer info must be verified with photo. Scratch test or magnet test
The water supplier must provide instructions to the building owner and must receive photo or other documentation clearly showing the service line material. When piping material is difficult to categorize visually, a scratch test, magnet test, or other verification must be conducted and documented.

## Slide 19: OAR -333-061-0036 (10)(h)(A)(ii) Continued:
(V) Portion of service line IF jointly owned –
excavate at one location per ownership
(VI) Methodologies used according to rule – NO Lead Service Lines - Identified
  Random Sampling – UNK lines - 95% confidence physically inspected – last resort
  Remaining UNK lines deemed NON-LEAD
  Noted on Spreadsheet
Notes: Per rule methodologies
Expose to verify materials -
AT the foundation, caution with private property and Uniform plumbing code
If No LEAD discovered then use the methodologies listed, random sampling of UNKs for 95% confidence level must be PHYSICALLY inspected
(V) Each service line, or portion of the service line if jointly owned, may be excavated, or exposed at one location such that the material can be identified, or the water supplier may inspect the service line as it enters the building.
(VI) If no lead service lines were identified using the methodologies listed in sub-subparagraphs (10)(h)(A)(ii)(I) through (V) of this rule, a random sampling of a portion of the remaining unknown service lines that provides a 95% confidence level must be physically inspected as specified in sub-subparagraph (10)(h)(A)(ii)(V) of this rule. If no lead service lines are found in the randomized pool, all remaining unknown service lines can be categorized as non-lead.

## Slide 20: How To Inventory
Records review
Installation date & diameter
Physical / visual inspection
  Scratch, Magnet
Statistical line sampling
Notes: How detailed, this may be a time to begin a better approach to mapping, record keeping, establish notes and build on
Key points are dates and pipe sizes, 2 plus inch if unlikely lead
Time, hours and personnel
Outline for statistical sampling on the State’s webpage

## Slide 21: Records Review - A
Service line installation records – After Jan 1, 1986 – NON-LEAD
  Two –inch diameter or larger – NON-LEAD – not strong enough for larger piping
Tap cards – standardizes pipe materials
Plumbing permits
Maintenance records
All documentation must indicate pipe material
Notes: Records review – self explanatory
Self explanatory
Points 2 through 4 are they available-?, legible, paper or electronic,

## Slide 22: Records Review - B
Meter installation records
Property tax records
Drawings or maps
Issues: may not be legible, complete, or accurate
Notes: Records review – self explanatory
Self explanatory
Points 1 through 3 are they available-?, legible, paper or electronic,

## Slide 23: Physical Inspections
Mechanical excavation
  Tried and True
  Reliable – high accuracy
  Time consuming
Hydro Vacuum excavation
  Alternative
  Time consuming
One location both sides PWS & customer
Notes: Mechanical – Physical inspection methods
Hydro-excavating – own equipment vs rental expense
One location
4.
Also dependent on personnel (total #), available equipment. Rentals, costs
Weather may impede progress, start early in the year

## Slide 24: Service Line Inventory Jargon -
Initial SL inventory completed (to the State) October 16, 2024
Lead Service Lines (Lead Service Lines)
Galvanized lines Requiring Replacement
Non-Lead
Unknown Service Lines (lead status) (UNK)
Notes: Reemphasizing the terms to understand the spreadsheet completion
Just another reminder of the deadlines, recommend having info to the State by early September
Where the SL is made of lead – any component
It is or was downstream of Lead Service Lines or UNK
Non lead evidenced based record, classifying actual material, PVC, CPVC, Copper, PEX, Muni-PEX
Classifying UNKNOWNS
  Not known to be lead, Galvanized Required Replacement or non-lead and no evidence documented

## Slide 25: Visual Testing
Scratch test – lead appears shiny when scratched
Magnet test – iron pipe is magnetic, lead pipe is not
Residential surveys
Photos (if from owner must have date stamp)
Plumbers
Notes: Visual Testing
Self explanatory on the first 2 points
….
Residential survey – time consuming, inaccurate, look at potential rate of return, 95 percentile is difficult
Photos, lots to consider, date stamped, clearly defined
Plumbers, local companies, are records allowed to be shared, cooperation

## Slide 26: Statistical Analysis – For Unknown Connections
No known Lead Service Lines - UNK – statistically verify – 95 percent confidence interval
Requires physical inspection
If ANY lead is found – UNK cannot be categorized as NON-LEAD
If ANY lead is found – method cannot be used
Statistical verification
    Less than 1500 unknowns – inspect 20%
    1,500 unknowns – inspect 322 for 95% confidence
    3,000 unknowns – inspect 341
    5,000 unknowns – inspect 361
    10,000 unknowns – inspect 381
Notes: Statistical –
  20 percent of UNK must be inventoried – and report by due date
  If deadline is not met all UNK lines must be inventoried
  Sites to excavate need to be randomly chosen – examples of total UNK need physical verification
  So, inventory is completed, an operator has UNK lines….20% to be verified

## Slide 27: HOW MANY?

## Slide 28: OAR -333-061-0036 (10)(h)(A)(iii)
(iii) Each service line, or portion of the service line where ownership is split, must be categorized in the inventory in the following manner:
(I) Lead – SL is made of lead
(II) Galvanized Requiring Replacement – downstream of Lead Service Lines or current from UNK
(III) Non-Lead –evidenced based proof NO lead, classified as Non-Lead
(IV) "Lead Status Unknown" where the service line material is not known to be lead, galvanized requiring replacement, or a non- lead service line, such as where there is no documented evidence supporting material classification.
Notes: (iii) Best understood that each side of the split should be noted – description on the EXCEL SPREADSHEET
(I) Known SL is made of lead materials -
(II) "Galvanized Requiring Replacement" where a galvanized service line is or was at any time downstream of a lead service line or is currently downstream of a "Lead Status Unknown" service line. If the water supplier is unable to demonstrate that the galvanized service line was never downstream of a lead service line, it must presume there was an upstream lead service line.
Non-Lead
Lead status unknown- where the service line is determined through an evidence-based record, method, or technique not to be lead or galvanized requiring replacement. The water system may classify the actual material of the service line (for example, plastic or copper) as an alternative to classifying it as "Nonlead." UNK – Lead Status Unknown" where the service line material is not known to be 1 of the 3 verification is required.

## Slide 29
Galvanized Line
Not GRR
Non- Lead

## Slide 30: Inventory Planning Stages
Planning – no approval necessary by DWS
Staffing – determine additional time – current workload - knowledge
Collect data – existing “available” or starting new
Considerations
  Approved methods
  Homeowner impacts
  Costs
Use DWS template – spreadsheet
1st priority – can this be completed with current resources?
Notes: Logistics to be considered as the Lead Service Lines inventories are managed
How you approach the inventory review does not need State approval
Whatever the consideration, consider adding 20 percent more time and dollars
Time factors are based on what info you can start with, complete inventory versus know nothing
…..
EXCEL created is very useful for step approach, good tool, but this project is still time consuming
What do you have to complete the process?......Consider State assistance
Per CFR –
Water systems with only non-Lead Service Liness are required to conduct an initial inventory, but they are not required to provide inventory updates to the state or the public and they may fulfill the requirement to the inventory publicly accessible with a statement that there is no Lead Service Liness, along with a general description of the methods used to make that determination.
One and Done!

## Slide 31: Drinking Water Services Website
www.Oregon.gov/LCRR
QR Code
Notes: Templates
  Available from the OHA-DWS, suggesting using the template – standard form
    Ease of use
  With the amount of information required, this State’s efforts support using the template
  Outlines the instructions for the spreadsheet, - descriptions, inventory sheet, replacement plan
    Consider using a tablet in the field to complete inventory

## Slide 32: QR Code – use Smart Phone to link to webpage

## Slide 33: Environmental Protection Agency’s Website - QR Code

## Slide 34: 120 Water – Contact Information

## Slide 35: Completed Spreadsheet Link
DWP.DMCE@odhsoha.Oregon.gov.
Notes:   1. E-mail address where inventory spreadsheet is sent

## Slide 36: Assistance
Free to systems serving <10,000 people
Training and outreach on service line inventory, methodologies, and reporting requirements
Individual assistance to public water systems
May also help with mapping of PWS facilities
Receiving assistance is first come first served
Notes: Available assistance
Pending the need, schedules will be based on efficient scheduling
On-site training for inventories, methods, and reporting
Consider this inventory task as a tool for future system data sets
Goal of this class is to reduce the time towards completion to meet the October 2024 deadline

## Slide 37: OHA DWS Assistance Continued
Oregon Association of Water Utilities – Zone 1
503-837-1212
HBH Engineering – Zone 2
503-554-9553
120 Water – Statewide
support@120water.com
Notes: Entities assisting the State to complete SL inventories by 10-16-2024
  Set up per region

## Slide 38
Notes: A map will give a visual to attendees

## Slide 39: Service Line INVENTORY (SL)
If Lead Service Lines, Galvanized Required Replacement or UNK, inventory info must be accessible to the public
Notification must be available to the public
For Lead Service Lines and Galvanized Required Replacement: The inventory must include an associated location identifier:
    such as a street address, block, intersection, GPS coordinates
Notes: Made available to the Public, details the lead and Galvanized Required Replacement
If found
Must include

## Slide 40: Discovery of Lead – 333-061-0036(10)(B)(i-iii)
B - Any lead pipes, similar components found in PWS must:
(i) Remove the component upon discovery.
(ii) Include the component info as part of a compliance schedule approved by the Authority according to OAR 333-061-0087(4); or
(iii) Include the component as part of the replacement plan described in paragraph (10)(h)(C) of this rule, for removal as quickly as feasible.
Notes: Self explanatory –
  If unable must set a schedule for removing and upgrade.
Include the component – clarify on the future list those components to be removed for the future.

## Slide 41: Discovery of Lead – 333-061-0036(10)(C)(i-viii)
This rule is being amended through the Lead Copper Rule Improvement due in the future
Notes: READ SLIDE

## Slide 42: Resources
EPA
  Internet search – EPA lead and copper rule
State of Oregon
  Internet search – Oregon lead and copper rule
AWWA (American Water Works Association)
  ASDWA (American State Drinking Water Administrators)
Internet search – AWWA or ASDWA lead and copper rule

## Slide 43: Oregon Template - Excel
Four Tabs – description, inventory, replacement plan, methodology – will be asked about methodology
Description – explains how the spreadsheet works
Inventory – Provides row for each service connection
Replacement plan – 7 key elements to follow
Methodology – outlines 3 categories
  Historical Records
  Normal Operations
  SL Investigations
Notes: Description – directions to complete the inventory
Information relating to each service connection.
Replacement plan info is on hold under revisions as supported in the “improvement” rule
Methodology – what approach was taken by PWS to complete the inventory

## Slide 44: Oregon Template - Excel
Black Font required for inventory and must be populated
Blue font - Useful for tap monitoring location determination - OPTIONAL
Green font - Good information for water system to know - OPTIONAL
Purple font - results are calculated by the spreadsheet using previous inputs.
SUMMARY TABLE MOST IMPORTANT to verify information

## Slide 45: Mandated Information

## Slide 46: Optional Information

## Slide 47: Mandated Summary

## Slide 48: Summary and Conclusion
October 16, 2024
Set plan in motion
Be aware of time, considering adding 20% more to complete
Consider additional operating expenses – non-routine task
Consider the budget, part-time personnel to assist
OHA-DWS and County REHS for additional assistance

## Slide 49: Resources
Oregon Association of Water Utilities - 503-837-1212
Zone One SW – South of Salem, Coastal
HBH Engineering – 503-554-9553
Zone Two NW to NE Oregon
120 Water – State – 120water.com
Thank you for listening!