## Criteria
Pump test are intended to provide aquifer & well information for groundwater resource characterization & to help solve well problems.
Forms can be sent to:
WRD_DL_pumptestsupport@water.oregon.gov
This pump test workbook contains 3 sheets (not including this sheet).
*clickable shortcuts
Remember, your pump test may not be approved unless it meets the following criteria*:
The dischage rate was held constant for the entire pumping phase.
The pump was on during the entire pumping phase (≥4 hours).
The discharge was measured at the start of pumping and at least once every hour during the test.
Water levels were measured to an accuracy of 0.1 feet or 0.5 percent.
Pre-test static water levels were measured at least three times in the hour before pumping began at no less than 20 minutes apart
Water levels were measured at the specified intervals during the pumping phase of the test for at least four hours.
(≤ 2 minutes for the first 10 minutes, ≤ 5 mins for 10-30 mins, and ≤ 15 mins for the remainder of the test)
Water levels were measured at the specified intervals (see above) during the recovery phase of the test for four hours
or until 90% of the maximum drawdown has recovered.
If using an airline, measurements were calibrated with an e-tape & the depth to water was ≥ 300 feet.
The pump test cover sheet was completely filled out and signed.
The pumping rate was as close as reasonably possible to the (anticipated) pumping rate during normal use of the well.
The well was idle for at least 16 hours prior to the test.
The pump test was completed by an acceptably qualified person
(Oregon licensed well constructors, Oregon registered professional geologists or engineering geologist, Certified water rights examiners, Oregon registered professional engineers)
*This checklist is inteded for information purposes only & does not guarantee a pump test approval. The Department reserves all authority
pertaining to the implementation of the rules under OAR 690-217.
Pump test requirements for OAR 690-217 can be found online here.
Cover Sheet
Methods Sheet
Data Sheet

## Cover Sheet
Owner / Business :
Name |  | Phone Number |  | Owner Street Address
State |  | City |  | Zip
If different from owner,
Test Conducted By |  | Qualifications |  | License #
Company |  | Phone Number |  | Company Street Address
Company State & Zip |  | E-mail
Tested Well Information :
Well Log |  | Well Log # |  | Well Tag L-#
Date Drilled |  | TWP RNG SEC QQ |  | Surveyed Location
Latitude |  | Longitude
Water Right(s) Information : | include letter in front (ex. G-xxxxx)
Application |  | Permit |  | Transfer
Certificate
I hereby certify that this test has been conducted in accordance with OAR 690-217:
Operator Initials: |  |  | Date:
Owner Initials: |  |  | Date:

## Methods Sheet
1 | Are there any wells, other than domestic or stock wells, within 1000' of the tested well?
2 | If yes, identify the well by OWRD log number. Note the approximatge distance to each well from tested well and approximate pumping rate.
|  | Well Log |  | Distance From Pumped Well |  | Date & Time Pump On |  | Pumping Rate
[5 empty] | ft |  |  |  | gpm
ft
ft
ft
3 | Is there a lake, stream, or other surface water body within 1/4 mile of the tested well?
|  | Approx. Distance |  | Approx. Elevation Difference
|  |  | ft |  | ft
4 | Was the test conducted during normal use of the well?
|  | Where pumped water was discharged? |  |  |  | How far from pumped well was water discharged?
ft
5
Water-Level Measurement Method
|  | Airline |  | If other, please state:
|  |  |  | If airline used, give length |  | (ft)
*Airline mmt must be verified by an e-tape mmt.
Verify Airline here:
[5 empty] | psi |  | ft
[5 empty] | E-tape |  | ft
If Pressure Transducer used,
Manufacturer:
Serial #:
Date Last Calibrated:
` |  |  |  |  | Units:
|  | Pump Type |  | Pump HP |  | Pump Set
ft
|  | If other, what pump type? |  |  | Idle Time | unit
Discharge Method
If Flowmeter used,
Manufacturer:
Serial #:
Date Last Calibrated:
Units:
|  | Measuring Point | (MP)
|  |  | ft |  | land surface
Description of MP
Time Pump Turned On
|  |  |  | Date |  | Time
Time Pump Turned Off
|  |  |  | Date |  | Time
|  | Total Pumping Time |  | Hours |  | Minutes

## Data Sheet
Excel Tips:
1.Duplicate cells by dragging bottom right corner of 2 highlighted cells of the same data
2. Quick time format cells by highlighting the cells with the time difference needed and dragging bottom right corner of highlighted cells (ex. 10:00 & 10:02 (highlight cells) > 10:04 (next cell))
3. Rows are can be added and deleted.
4. To save on paper, make sure to delete excess, unused rows prior to printing
*Measurements in decimal foot | [9 empty] | `
Date | Time | Depth to Water Below MP | Discharge Rate | Units | Pump ON / OFF | Airline (psi) | Flowmeter | Units | Comments

## Hydrograph
*Rough hydrograph using the Data Sheet to use as a review reference of the data entered.

## Sheet2 (hidden)
Business Partner | yes
Certified Water Right Examiner | no
Consultant | unknown
Driller
Other
Owner
Professional Engineer
Professional Geologist
Pump Installer |  | hours
Unknown | above | days
| below | weeks
BAKE |  | months
BENT
CLAC
CLAT | Airline
COLU | Electric Tape | (gpm) gallons per minute
COOS | Sounder | (gpd) gallons per day
CROO | Steel Tape | (cfs) cubic feet per second
CURR | Transducer
DESC | Other
DOUG
GILL | Centrifugal
GRAN | Jet | on
HARN | Submersible | off
HOOD | Turbine
JACK | Other (Enter)
JEFF |  | gallon
JOSE |  | acre ft
KLAM |  | cfs
LAKE |  | ain
LANE | Flowmeter
LINC | Manometer
LINN | Vol/Time
MALH | Other (Approved)
MARI
MORR
MULT
NLOG
POLK
PROP
SHER
TILL
UMAT
UNIO
WALL
WASC
WASH
WHEE
YAMH